## Sheet1
ITEM | DESIRED STANDARD | COMMENTS
Required design parameters | Colebrook White Coefficient of k = 0.0015m for concrete pipes. | Councils usually adopt k = 0.006m for their concrete pipes.
Manning’s n for floodways:
n = 0.025 for roadways
n = 0.035 for grassed reserves
n = 0.015 for concrete channels
n = 0.050 for floodplains and cleared rural paddocks
For safety in floodways, v x d must not exceed 0.35.
Embedment and backfill of pipe systems | Refer to AS3725 and the Concrete Pipe Association of Australasia Manual. See Section 5.3.4 Structural design for an example. | Scoria is not typically acceptable by Melbourne Water. Permission must be given by Melbourne Water prior to construction.
Reinforcement cover in corrosive environment | Minimum clear cover to steel reinforced concrete pipes is listed in AS4058 as being 10mm for most flushed jointed pipes. | May increase cover to up to 25mm if the pipe is subject to corrosion by salt water or other aggressive ground water.
Cement type | Type GP (general purpose) under normal circumstances.
Type SR (sulphur resisting cement) if there are aggressive ground conditions.
Splays | Minimum splay radius (along pipe centerline) = 8D.
Maximum deflection per joint is approximately 5o.
Bandage joints | Refer to MW standard drawing 7251/8/308. Maximum deflection per joint (degrees) = (18-D/150) where D is in mm.
Associated concrete structures | Minimum strength grade of 32MPa. Higher grades may be required depending on the circumstances. See Table 1 of Section 5.3.4 Structural design for example in-situ structures.
Pipe outlets to a waterway | Outlet velocity should be reduced to less than 1.5m/s. If velocity is greater than 1.5m/s then it needs to be slowed using drop structures, energy dissipation structures, large flat pipes and large rocks. Rock beaching may also be required for scour protection.
| Maintenance access to the outlet structure must be provided. | Maintenance crews need safe access down to outlet and firm base at the pipe outlet to stand on to enable pipe inspection, i.e. a concrete apron.
Safety fencing may be required depending on the height of the drop.
Pit sizing specifications | For single chamber (e.g. manhole, junction & side entry pits) minimum internal dimension is 900mm x 900mm. Opening 750mm x 750mm, haunched, edge aligned with chamber side containing step irons. | Minimum sizing to provide safe access for average persons with equipment.
| NOTE: Where a chamber includes a valve, dimensions must increase to be a minimum of 1200mm x 900mm to accommodate loss of working space. | Note step irons protrude 300mm from chamber face. Valves that are to be located in the pit structure will take up additional working space.
| For multi chamber (e.g. twin function pits, weir pits) each chamber must be 900mm x 1200mm. Opening 750mm x 750mm for each chamber, aligned with step irons. If pit takes in overland flows, Pipe Grille required as per intent of standard drawing | Minimum sizing to provide safe access for average persons with equipment.
| 7251_08_319_Pipe_Grille_Type2_(900x900) | Note step irons protrude 300mm from chamber face. Valves that are to be located in the pit structure will take up additional working space.
Step irons to:
| - be at 300mmm spacing (commencing from top of pit) in a straight continuous line | Access requirement.
| - extend to 300mm from pit floor | Access requirement (valve is 300 x 300mm).
| - have sufficient clearance from outlets, valves and haunches. | Safety requirement.
| Pipes entering pits to have a 150mm internal space from outside of pipe to pit corner for structural stability, i.e. pit minimum size = 150 + t + D + t + 150 (where ‘t’ = thickness of pipe wall). | Ensures structural integrity of the pit
Normally manholes to be separated by a distance of 80 to 100D (nominal internal diameter), maximum 200m. Spacing should reduce to 50m maximum in heavy industrial areas. For these cases contact Melbourne Water for required spacing.
Precast pits | Melbourne Water acceptance must be obtained for use of all precast pits prior to construction.
Pit design | No pipes are to enter through pit corners.
| Unless the pit is designed to surcharge, HGL for the design storm event shall not be higher than the finished surface level, ensuring pit lids don't blow. | Transitions flow downstream, improves efficiency.
| A concrete chase/shaping of base to transition flows is acceptable. | Increases asset life.
If pit takes in overland flows, pipe grille required as per intent of standard drawing
7251_08_319_Pipe_Grille_Type2 (900x900).
Pipe grilled pits require 300mm wide concrete apron and/or fence surrounds as dictated by maintenance needs of the pit’s location.
If the pit doesn’t take overland flows, visual inspection capability is required and a grated style cover constructed from flat bars is to be utilised.
| Fasteners and hardware installed in pits should be hot dipped and galvanised rather than zinc plated. | Has a greater coating thickness and therefore extends the lifespan.
Confined space entry needs to be considered. Recommend including an anchor point cast into top of precast unit. Alternatively, install an anchor point nearby.
| Sacrificial mass concrete in the base of a drop structure due to grade or velocity is acceptable to Melbourne Water | Increases the asset life of the pit.
Twin function pit design (for wetlands) | Twin function pit (internal, each chamber) dimension is 900mm x 1200mm. Lid is to be grilled/grated to enable visual inspection.
Contains a concrete divider wall.
Chambers adhere to pit size specifications.
Contains a resilient seat gate valve with spindle (stem cap) extending to top of pit unobstructed by lid structure.
Gate valve spindle is to be sized for a 35mm square key extending up to within 50mm of bottom surface of grille with opening cut out above. Valve located on downstream side of divider wall.
| Valve is to be offset horizontally from baffle plate over flow. | Enables operation of valve without opening grille lid.
| Metal baffle plate attached to an oversized concrete opening preferred. Metal plate to be installed to the upstream side of wall, bolt mounted. | Metal plate preferred as it enables easy modification to control future flow regime.
| Plate to contain a single opening shaped and dimensioned to allow a desired staged drawdown for water quality outcomes. | A plate with a single opening is less likely to block with debris than a plate with holes.
| Outlet pipe capacity to be suitably oversized to enable future adjustment of plate if necessary. | An elbow or riser (PVC or concrete) is not preferred as this is a fixed aperture and is difficult to adjust later if needed.
Temporary outfalls | Batters slopes to be 1 in 3 or flatter. | Minimum requirement for public safety. Situations where soil profile contains rock may be assessed on a case-by-case basis. Porous rock wall must not impact the hydraulic functionality of the outfall, i.e. they should only be placed in the invert of the channel, not up the batter. They must allow high flows to pass.
| Must be hydro seeded and or have geotextile fabric surface protection. | Assists with preventing erosion of batters.
| Free draining outfall required. | Prevents flooding of the estate/stage.
| Porous rock bunds (rock wrapped in geo tech fabric) implemented at appropriate intervals to control sediment. | Assists with removing sediment from the waterway (environmental control). Prevents sediment from leaving site. Refer to EPA publication ‘Doing it right on subdivisions’.
Note: Wrapped porous bunds to be kept relatively low, 300-350mm in height with middle section constructed lower at 225-275mm to direct flows over top centre section of structure.
| Sump or sediment pond constructed at downstream end. | For sediment control.
| Bunding above top of batter. Flows to be directed to controlled discharge location with appropriate scour protection. | Prevents overland flows scouring batters.
| Fencing is installed where there is a fall from height hazard, outfall is permanently inundated, or if vehicle exclusion is necessary (i.e. all batters 1:3 or steeper). | For public safety, contractor safety, and traffic exclusion.
Note: If estate boundary is fenced for public safety or other reasons, para webbing of temporary outfall is required for contractor safety.
Flows to be directed to controlled discharge location with appropriate scour protection.
Duration of outfall drain determined & accepted.
All land owner consent to the outfall must be submitted in writing prior to works commencing.
Developer/authority who is to maintain the outfall accepts design and ongoing maintenance in writing prior to construction commencing.
Batter slopes (waterways and reserves) | Option 1: Grassed batter slopes to be 1 in 5 or flatter. A 3m run out area at the bottom of the slope is to be provided so MW can mow up and down if necessary. Run out area is to be a maximum grade of 1:12 and be clear of rocks, trees, fences etc. | Allows for safe slasher / mower operation. MW uses the following grass cutting machinery:
· Tractor slashers
· Tractors with reach mowers
· Out front mowers
· Zero turn mowers
· Brush cutters
Note: Specialised slope mowers and remote controlled slope mowers are not used.
Option 2: Grassed batter slope is a maximum grade of 1:12 to allow for safe grass cutting (horizontal and vertical cutting method). No run out area is required, area must be clear of rocks, trees, fences, drops etc.
For mowing around vegetation MW requires a 3m gap between vegetation to allow mower access. Overhanging vegetation can be an access issue.
| Slopes steeper than 1 in 5 to be densely vegetated. | Eliminates mechanised maintenance and deters entry by general public (fencing may also be required).
Note: Where overland flows will scour batters due to steep grade, rock armouring or hydro seeded buffer zones may be necessary.
Waterway crossings (bridges / culverts) | Refer to Waterway crossings. | MW will not accept pipe outlets underneath boardwalks or bridges.
Waterway pipeline crossing | Refer to Waterway crossings. | No open cutting or covering is to occur without prior approval.
Utility installation nearMelbourne Water assets | Refer to Utility installations near sewers, drains and water mains.
Building over Melbourne Water assets | Refer to Works on or near drains, water mains and other assets.
Shared pathways | Refer to Shared Pathway Guidelines. Also refer to the Bicycle Network website.
Planting near sewers, drains & water mains | Refer to Planting near sewers, drains and water mains.
Rock work embedment & void filling (FCR mix) | Fine crushed rock between 0–150mm (including fines). | Voids between rocks filled (prevents undermining).
| 150mm thick embedment layer required below rock layer, excluding toe & edge rock. | If rock work appears excessive check the shear stress output (HECRAS) to ascertain problematic areas.
Nib wall in rock chutes | Must be constructed using concrete.
| Flanks to be constructed a minimum of 300mm vertically higher than the crest. | Prevents outflanking of nib wall.
| Embed minimum 500mm into in situ soil both at the batters and invert. | Prevents undermining of rock chute.
| A cement-based slurry seal should be poured on either side of concrete nib wall to seal first layers of rock beaching. | Top of nib wall can be finished with mixed in gravels / small rock to achieve aesthetic appeal and correct FSL.
Rock chute planting | No planting is permitted in the low flow channel. | Undermines the rock chute. Voids must be filled with graded rock.
| For rock work above low flow channel, where planted, voids between the rocks filled with a mixture of FCR & soil (70:30) mix or quarry scalpings. Planted void containing soil/FCR mix extends no more than 50% of depth of rockwork. | Allows establishment of plants (above low flow area).
Sediment pond base | Hard base required (concrete slab as per below, or layer of rock 300-400mm thick), continuing 300mm vertically up the batter (no embedment layer is required). | Hard base provides physical feedback to excavator operator whilst desilting, ensuring clay liner will not be breached. Crushed concrete rubble or coloured sand are not permitted.
Concrete / Shotcrete acceptable.
Concrete must be steel reinforced 150mm thick, 32MPa concrete mix, SL72 steel grid reo.
Rocks must be 300-400mm thick, with length and width > than thickness, i.e. broad flat rocks.
Sediment pond access track | Track to continue down into the invert of the sediment pond in accordance with heavy vehicle standards. | Allows for desilting of the sediment pond.
Note: Concrete is not an acceptable access track material as this will be prone to cracking under the weight of an excavator and trucks.
1 in 5 max grade, min 4m wide, with provision for turnaround area for a tandem (10m) tipper once off the road.
Do not construct using concrete as this will be prone to cracking under the weight of an excavator and trucks.
| Integrity of maintenance track shall not be compromised in any weather conditions. Typically requires 200mm depth compacted FCR. | The use of scoria for maintenance access tracks is not acceptable to Melbourne Water.
Where longitudinal grade exists on path, FCR mix must be cement stabilised (6%), including below NTWL.
| Bollards must be located on either side to indicate where the track is below NWL. Acceptable options for bollards are recycled plastic or treated pine. | Do not use hardwood or steel.
Sediment removal excavator reach | MW excavator max reach is 7m from access. | If access doesn't allow desilting within 7m reach from outside pond, then the access path must extend down into the invert. Long reach excavators are not typically utilised by MW.
Sediment pond drying | Option 1) Insitu dry out facilities enabling diversion of low flows around sediment pond, e.g. pipe & valve. | MW operations budget does not accommodate transport of wet material. Eduction is not an option.
| Option 2) Sediment dry out area suitably sized to accommodate 150mm depth of piled sediment. | Do not locate the dry out area on a peninsula.
- located above Q10 level
- position to avoid excessive machinery movement (close to pond)
- easy access for removal of dry sediment and turn over during drying period.
Maintenance tracks - heavy/large vehicle access | Width (min) 4m, plus turning circle.
Reinforced to take 20T vehicle. Ensure pipes under track are protected from loading of vehicles.
| Integrity of maintenance track shall not be compromised in any weather conditions. Typically requires 200mm depth compacted FCR. | The use of scoria for maintenance access tracks is not acceptable to Melbourne Water.
| At road edge, require industrial crossover to Council standard and rolled kerb adjoining it. | Concrete not acceptable unless covered by council for maintenance under a shared path agreement.
| Bollards are required to prevent unauthorized access. Acceptable options for bollards are recycled plastic or treated pine. | Do not use hardwood or steel.
Maintenance tracks - light vehicle access | Width (min) 4m, with provision for turn-around area. | Allows a light vehicle to access asset to undertake maintenance.
Loading typically ~2T, e.g. ute.
| The integrity of the maintenance track shall not be compromised in any weather conditions. Typically requires 200mm depth compacted FCR. | The use of scoria for maintenance access tracks is not acceptable to Melbourne Water.
Where longitudinal grade exists on path, FCR mix must be cement stabilised (6%).
| Bollards are required to prevent unauthorized access. Acceptable options for bollards are recycled plastic or treated pine. | Do not use hardwood or steel.
Maintenance track access exclusion | Bollards or gate to prevent unauthorised access. Typically dual lock (Council / MW) but there may be more parties. | Allows both MW & Council access to asset as required.
Public vehicle exclusion - completed works | Public vehicles are to be prevented from accessing the reserve from adjacent roads. Use fence, bollards, rocks, etc.
Pipe outlets to a waterbody | Preference for invert to be no lower than 100mm below normal water level of receiving water body, can be reviewed on a case-by-case basis. | Due to safety limitations and slasher / mower operation.
| Include fencing around all pipe outlets to ensure safety, e.g. fall protection. | Large pipes can be large enough to walk up. Grated or grilled outlet covers not acceptable if they could impede escape from pipeline for any persons trapped.
Note: In some instances (e.g. large diameter pipes) it is desirable for safety reasons to have invert of the pipe below NWL as it acts a deterrent for public access to the pipe.
Wetland & RB (General) | Review documentation required for design, ascertain if it meets wetland & RB design requirements, e.g. Geo report, ANCOLD, flora & fauna, MUSIC model, HECRAS, RORB, AAV, SEMP. | Geo report should determine if a clay liner is required
Wetland balance pipes | 300mm dia minimum. | Smaller than 300mm is likely to block.
| Balance pipes to be RCP (reinforced concrete pipe) IJ (interlocking joint). | PVC (polyvinyl chloride) and HDPE (high density polyethylene) pipes (e.g. Iplex) not permissible for balance pipes.
| Inlet & outlet invert set 300mm above pond invert. | Ensures consistent water level throughout system.
Enables gravity drawdown of ponds.
Prevents sediment accumulation, plant growth and blockage of pipe.
| Use pre-cast concrete headwalls & or 'truncated pits'. | Rockwork end walls not permissible due to vegetation build up on sediment collecting on rock.
| Balance pipes should not connect into a sediment pond. | Due to siltation issues and inability to isolate the sediment pond during maintenance.
| A guide post / bollard required at either end of balance pipe protruding above NWL to show location. Acceptable bollard options are recycled plastic or treated pine. | Do not use hardwood or steel.
Planting mulch & jute mat | Jute mat to be installed in planted areas above TEDD for wetlands. | Allows colonisation of ephemeral & aquatic plants. No mulch to be placed below TWL or frequently inundated areas.
| Jute mat to be installed in planted areas across frequently inundated level for waterways and channels. Limit application of loose mulch to planted areas above Q100 levels. | Enhances plant establishment by suppressing weeds and retaining moisture, prevents scouring & erosion of waterway.
| Jute mat must be installed to the manufacturer’s specifications, including fasteners. | Jute mesh (loosely woven jute strings) is not to be applied in isolation. Must be designed to hold mulch in place.
Wetland boardwalks / viewing platforms | Refer to Chapter 7 of our Shared Pathways Guidelines. | Clear span & single pier construction is required to reduce the likelihood of debris blockage. We will not accept pipe outlets underneath boardwalks, structures over sediment ponds or structures over weir crests.
| In addition to section crossing the pipe, any structural type asset will require removable panels above. | Removable decking panels required as machinery / lifting access not possible below boardwalk.
| Require Council's written acceptance of all boardwalks, viewing platforms and feature poles prior to construction. | Council is asset owner and maintainer, and therefore boardwalk must be designed to their standards and maintenance requirements.
Design comments to specify that footings must be installed by civil contractors to avoid damage and rework.
Islands within wetlands | MW will not accept islands within wetlands. | Difficult to maintain (need a boat). Can become overgrown with weeds.
Physical barrier standard (including fencing) | Refer to the Safety and Maintenance section and standard drawings for detail.
Retarding basin design | Refer to Guideline for the Design and Assessment of Flood Retarding Basins.
MW will require:
- submission of ANCOLD 'Hazard Assessment' submitted as per Guideline
- submission of design in accordance with the Guideline
- submission of design report in accordance with Chapter 7 of the Guideline
| Retarding basin design requires input from an engineer with experience in dams. Unless the consultant has previously submitted work accepted by MW, we will insist on the design being peer reviewed by a consultant that has this qualification. | Please contact the MW Developer Project Works Team for details.
| Planting on retarding basin embankments is to be limited to grass only. | Trees which die leave rotting root systems that act like conduits through the embankment. Shrub cover hides early signs of a potential dam failure.
Bio retention systems | Refer designer to use http://www.monash.edu.au/fawb/products/. | Measures must be put in place during and following installation of the BRS to ensure that it is protected from sedimentation.
Culverts | Pipe culverts to be used in preference to box culverts. | Pipe culverts are cheaper and easier to install. Box culverts only be accepted in situations where available cover is limited.
Box culverts must be installed by an open cut method of construction. The slab should be precast type.
If boring is required, pipe culverts must be used.
| When three or more box culvert cells are required, a link slab is to be utilised to create the intermediate cells. | Reduces cost of supplying box culvert cells considerably.
| Where there are two or more box culvert cells one of the cells should be lower (dropped cell). | Caters for normal (low) flows.
| Habitat values of waterway need to be considered, e.g. will length and arrangement of proposed culvert crossing have an adverse impact on local habitat populations, e.g. growling grass frogs and fish? | As directed or recommended by bio-diversity report.
| Subject to bio-diversity needs, inlet and outlet of culverts should be drowned out with a shallow water body. | Deters public access.
| Where public access is encouraged (e.g. an agreement with Council for the culverts to be used as an underpass for pedestrians and cyclists) the culvert cell being used should be offset from the others and be designed to be the last cell to start flowing in large storm events. | Safety provisions must be installed, including signage, barriers that can be deployed if underpass is flooded, and approaches that give the public adequate warning (line of sight) to the hazard.
Formal maintenance access track not required for culverts, but consideration must be given to maintenance access, e.g. along the invert of the waterway.
| Culvert design must consider both inlet control and outlet control ensuring culvert efficiency and that the flood levels of the upstream and downstream properties are not compromised. | Inlet control occurs when the capacity of the culvert is governed by the conditions on the upstream side of the culverts, i.e. the area, shape and edge details of the inlet face.
Outlet control occurs when the capacity of the culvert is governed by the depth of flow and velocity head at the outlet plus resistance loss for flow through the culvert.
Charts can be used to determine which of these controls applies.
Further details regarding the design of culverts may be found in Chapter 5B of the Austroads Road Design Guidelines.
Site environmental management plan | A Site Environmental Management Plan (SEMP) is to be available prior to works commencing. Must identify all areas of significance that may be impacted by construction and measures to be employed on site. A template is available from the Planning & Building website. | MW / EPA requirement.